# Evanston Fire and Life-Safety Services

# TENT INSPECTIONS

Date:

Inspector:

Event:

Location:

Operator’s Name:

Phone:

Comp    N/C     NA      Code Section

| - The tent/canopy shall be composed of flame-resistant material or shall be treated with a flame retardant. The tent/canopy should have an affixed label. |  |  |  | IFC-3104.2 |
| --- | --- | --- | --- | --- |
| - Portable ABC fire extinguishers shall be provided in conspicuous locations and mounted. 10 pound or K-Type extinguisher |  |  |  | IFC-3104.12 |
| - Tents where cooking is performed shall be a minimum of 20 feet from all other tents and must be approved for use by the Fire Prevention Bureau. |  |  |  | IFC-3104.15.5 |
| - Equipment used for cooking shall be vented to the outside and equipped with spark arresters (when required). Vents/Flues shall be a minimum of 12 inches from the tent. |  |  |  | IFC-3104.15.2 |
| - Outdoor cooking shall be performed a minimum of 20 feet from tents. |  |  |  | IFC-3104.15.6 |
| - Cooking and heating equipment shall be a minimum of 10 feet from exits or combustible materials |  |  |  | IFC-3104.15.3 |
| - LP-gas containers less than 500 gallons shall be a minimum of 10 feet from tents. LP-gas containers greater than 500 gallons shall be a minimum of 25 feet from tents. |  |  |  | IFC-3104.16.2 |
| - Flammable/Combustible liquids shall be stored outside in an approved manner a minimum of 50 feet from tents. |  |  |  | IFC-3104.17.2 |
| - Refueling of flammable-liquid-fueled equipment shall be done a minimum of 20 feet from tents. |  |  |  | IFC-3104.17.3 |
| - Generators and similar items shall be a minimum of 20 feet from tents. |  |  |  | IFC-3104.19 |
| - Multiplex power strip with surge protection or temporary wiring approved by the fire code official shall be used. |  |  |  | IFC 605 |
| - Electric heaters shall be labeled; and be connected to electricity by a cable suitable for outside use and sufficient size to handle the load. |  |  |  | LSC-11.11.6.2 |
| - Floors within tents and the ground outside tents within a 30-foot perimeter shall be kept clear of combustible waste. |  |  |  | IFC-3104.22 |
| - The means of egress shall be free of obstructions and tripping hazards at all times. Guy wires, guy ropes, and other support members shall not cross a means of egress at a height of less than 8 feet. |  |  |  | IFC-3103.12.8 |
| - Smoking shall not be permitted in tents. |  |  |  | IFC-3104.6 |
| - Means of egress must be illuminated with the fixtures supplied from a separate circuit or source of power. |  |  |  | IFC-3103.12.7 |
| - Tents shall be adequately roped, braced, and anchored to withstand the elements of weather and prevent against collapsing. |  |  |  | IFC-3103.9 |
| - Exit doors (if any) shall swing in the direction of exit travel. |  |  |  | IFC-3103.12.4 |
| LARGE TENTS |  |  |  |  |
| - Exit signs shall be installed in tents that hold 50 or more occupants. |  |  |  | IFC-3103.12.6.1 |
| - Exit signs shall have an emergency backup power system in tents that hold 300 or more occupants. |  |  |  | IFC-3103.12.6.1 |
| - An air-supported structure that holds more than 50 occupants shall have at least two blowers that each has a capacity to maintain full inflation. |  |  |  | IFC-3103.10.3 |
| - Tents with an area of 15,000 square feet or greater shall be located a minimum of 50 feet from a building or another tent. |  |  |  | IFC-3103.8.3 |
| - Exits shall be spaced so that all points within the tent are 100 feet or less from an exit. |  |  |  | IFC-3103.12.1 |
| - An emergency action plan and a site safety plan needs to be provided |  |  |  | IFC 403.2 |
| - Standby personnel required |  |  |  | IFC 3104.20 |
| - Crowd managers required |  |  |  | IFC 3104.20.2 |

Additional Comments: ________________________________________________________ ________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________