
[image: image1.jpg]


Evanston Fire and Life-Safety Services
TENT INSPECTIONS

	Date:                                        

	Inspector:                 

	Event:

	Location:

	Operator’s Name:

	Phone:


                                                                                    Comp    N/C     NA      Code Section
	1) The tent/canopy shall be composed of flame-resistant material or shall be treated with a flame retardant.  The tent/canopy should have an affixed label.  
	
	
	
	IFC-3104.2

	2) Portable ABC fire extinguishers shall be provided in conspicuous locations and mounted.
10 pound or K-Type extinguisher
	
	
	
	IFC-3104.12

	3) Tents where cooking is performed shall be a minimum of 20 feet from all other tents and must be approved for use by the Fire Prevention Bureau.
	
	
	
	IFC-3104.15.5

	4) Equipment used for cooking shall be vented to the outside and equipped with spark arresters (when required).  Vents/Flues shall be a minimum of 12 inches from the tent.
	
	
	
	IFC-3104.15.2

	5) Outdoor cooking shall be performed a minimum of 20 feet from tents.
	
	
	
	IFC-3104.15.6

	6) Cooking and heating equipment shall be a minimum of 10 feet from exits or combustible materials
	
	
	
	IFC-3104.15.3

	7) LP-gas containers less than 500 gallons shall be a minimum of 10 feet from tents.  LP-gas containers greater than 500 gallons shall be a minimum of 25 feet from tents.  
	
	
	
	IFC-3104.16.2

	8) Flammable/Combustible liquids shall be stored outside in an approved manner a minimum of 50 feet from tents.
	
	
	
	IFC-3104.17.2

	9) Refueling of flammable-liquid-fueled equipment shall be done a minimum of 20 feet from tents.

	
	
	
	IFC-3104.17.3

	10) Generators and similar items shall be a minimum of 20 feet from tents.
	
	
	
	IFC-3104.19

	11) Multiplex power strip with surge protection or temporary wiring approved by the fire code official shall be used.
	
	
	
	IFC 605

	12) Electric heaters shall be labeled; and be connected to electricity by a cable suitable for outside use and sufficient size to handle the load.
	
	
	
	LSC-11.11.6.2

	13) Floors within tents and the ground outside tents within a 30-foot perimeter shall be kept clear of combustible waste.
	
	
	
	IFC-3104.22

	14) The means of egress shall be free of obstructions and tripping hazards at all times.  Guy wires, guy ropes, and other support members shall not cross a means of egress at a height of less than 8 feet.
	
	
	
	IFC-3103.12.8

	15) Smoking shall not be permitted in tents.
	
	
	
	IFC-3104.6

	16) Means of egress must be illuminated with the fixtures supplied from a separate circuit or source of power.
	
	
	
	IFC-3103.12.7

	17) Tents shall be adequately roped, braced, and anchored to withstand the elements of weather and prevent against collapsing.
	
	
	
	IFC-3103.9

	18) Exit doors (if any) shall swing in the direction of exit travel.
	
	
	
	IFC-3103.12.4

	LARGE TENTS

	19) Exit signs shall be installed in tents that hold 50 or more occupants.
	
	
	
	IFC-3103.12.6.1

	20) Exit signs shall have an emergency backup power system in tents that hold 300 or more occupants.
	
	
	
	IFC-3103.12.6.1

	21) An air-supported structure that holds more than 50 occupants shall have at least two blowers that each has a capacity to maintain full inflation.
	
	
	
	IFC-3103.10.3

	22) Tents with an area of 15,000 square feet or greater shall be located a minimum of 50 feet from a building or another tent.
	
	
	
	IFC-3103.8.3

	23) Exits shall be spaced so that all points within the tent are 100 feet or less from an exit.
	
	
	
	IFC-3103.12.1

	24) An emergency action plan and a site safety plan needs to be provided 
	
	
	
	IFC 403.2

	25) Standby personnel required 
	
	
	
	IFC 3104.20

	26) Crowd managers required
	
	
	
	IFC 3104.20.2


Additional Comments: ________________________________________________________ ________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________
4/23/2014
4/23/2014


